## Overview
Eco-label for "heat pumps" | This document is valid without signature once uploaded by the applicant in the web portal | Please note that there are several sheets! | Please use this form only
Annex 1 to the contract according to DE-UZ 230 | The light blue fields are fill-in fields
Manufacturer (signatory): | complete address
Brand name
Trade name
Product Name:
KW output of the HP:
One series is to be certified
Production site: | complete address
2 Scope
These Basic Award Criteria apply to mass-produced heat pumps with an electrically driven com-pressor that are designed for heating rooms either with or without domestic water heating. This includes air/water heat pumps, brine/water heat pumps and water/water heat pumps with a nominal heating output of up to 70 kW (for outputting heat to water-based heating circuits in accordance with the nominal standards in EN 14511-2).
The following HP is applied for:
Air/water HP
Brine/water HP
Water/water HP
with hot water preparation
without hot water preparation
the HP has an electrically driven compressor
Comment:
The following do not fall under the scope of these Basic Award Criteria:
· Reversible air/air heat pumps
· Air/air heat pumps that utilise exhaust air
· Hybrid systems
· Pure industrial water heat pumps

## Requirements
Eco-label for "heat pumps"
Annex 1 to the contract according to DE-UZ 230 | The applicant confirms compliance with the requirement | The applicant confirms that this requirement does not need to be met | Additional attachments | Comment field
3.1 Refrigerant
The heat pumps must be free of refrigerants containing halogens.
chemical name of the refrigerant:
industrial designation of the refrigerant:
SDS is attached
GWP value(100 according to IPCC AR 6):
3.2 Energy efficiency
The heat pumps must have a seasonal coefficient of performance (SCOP) for average climatic conditions of at least:
A test report on the determination of the efficiency values of the heat pump according to DIN EN 14825:2019-07 and DIN EN 14511:2019-07 in a testing laboratory accredited according to DIN EN ISO/IEC 17025:2018-03 is enclosed.
3.3 Energy efficiency display
The devices have an energy efficiency display
Energy consumption also includes auxiliary power required to operate electric heating elements and heat source pumps.
The display shows the measured average energy efficiency, by month or quarter and by calendar year
The display shows the ranking of the measured energy efficiency against an expected value
The data is collected at regular intervals and can be read out in a freely available data format
The operating instructions contain information on the method of determining the energy efficiency, the balance limit and notes on possible causes of low efficiencies as well as suggested actions to remedy them or have them remedied by qualified personnel.
The data format and notes on readability for users are included in the operating instructions
A description of the energy efficiency display (with photo) and the relevant passages from the operating instructions are attached
3.4 Noise emissions
a.) The A-weighted sound power level (LWA) outside measured according to DIN EN 12102-1:2018-02 is:(specification in dB(A))
Maximum expected sound power level:(specification in dB(A))
Sound power level during night operation:(specification in dB(A))
A test document on the determination of the A-weighted sound power level (LWA) according to DIN EN 12102-1:2018-02 of a testing laboratory accredited according to DIN EN ISO/IEC 17025:2018-03 is attached
b.) The installation instructions contain clear instructions for selecting the installation site and for low-noise installation indoors and outdoors
The corresponding passages from the installation instructions are attached
3.5 Measures to guarantee the efficient and stable operation of the heat pump over many years
a.) A warranty of spare parts availability (equivalent) and software updates (functionality) for at least 15 years after the devices have been placed on the market is confirmed.
b.) A document marked as a user manual contains clear indications of which setting options can influence efficiency positively or negatively (e.g. if a mode can be set in which heat generation is only taken over by the heating rod)
The user manual contains clear indications of when it makes sense to set reduced night operation (e.g. indications of the state of renovation of the building, type of radiators, etc.).
The corresponding passages from the user manual are available
3.6 Services
The applicant itself or a contracted service partner provide services that ensure environmentally sound design and reliable and energy-efficient operation of the heat pumps.
If service partner, please provide company address:
a) The manufacturer offers tools and training for professional planning, installation including hydraulic balancing, maintenance and disposal of the heat pumps by specialist companies.
When commissioned by a specialist company, the manufacturer can check relevant parameters remotely and adjust settings if necessary.
b.) The applicant shall provide quotes of various maintenance contracts through manufacturers or qualified professional contractors.
The offer also includes the audit in accordance with the Building Energy Act § 60a after a complete heating period, but no later than two years after commissioning.
The audit is repeated regularly, this can also be done remotely.
c.) Offer of maintenance service available during normal customer service hours is confirmed.
3.7 Model series
The applicant shall provide the test documents required by point 3.2 and point 3.4 for at least 33% of the devices in the series
For the other devices of the series, the applicant shall provide product documentation showing that these devices also meet the requirements according to point 3.2 and point 3.4
It must be evident from the documentation submitted that the equipment represents a series.
general comment:
Note on A9: The heat pumps must have a seasonal coefficient of performance (SCOP) for average climatic conditions of at least: Application in: Use in a medium temperature range (55 °C) Use in a low temperature range (35 °C) Air/water heat pumps 3,3 (corresponds to s = 130 %) 4,6 (corresponds to s = 180 %) Brine/water heat pumps and direct exchange/water heat pumps 3,7 (corresponds to s = 140 %) 5,3 (corresponds s = 205 %) Water/water heat pumps 4,2 (corresponds to s = 160 %) 6,2 (corresponds to s = 240 %)
Note on A16: Example: good - a little too low (means: "check on occasion") much too low (means: "take action")
Note on A22: maximum of 60 dB(A) for units up to and including 20 kilowatts of power and 65 dB(A) for units 20 kilowatts and above.
Note on A42: Based on individual tests according to EN 14511/EN 14825 (see point 3.2) and EN 12102 (see point 3.4), the eco-label can also be awarded for a series. The number of devices to be tested within a series is at least 33% (rounded up to the next whole number). A series is defined in accordance with the European Quality Label for Heat Pumps and the European KEYMARK Scheme for Heat Pumps by the same heat source used and by the same refrigeration circuit concept (structure of the refrigeration circuit; design and construction; performance profiles of heat exchangers and compressors; control variables and control curves).

## Template
yes
no