## Overview
Eco-label for "Chillers" | This document is valid without signature once uploaded by the applicant in the web portal | Please note that there are multiple sheets! | Please use this form only
Annex 1 to the contract according to DE-UZ 231 | The light blue fields are fill-in fields
Manufacturer (signatory): | full address
Brand name:
Trade name (if different from brand name):
Product description:
A series is requested:
Production location: | full address
2 Scope
In the context of the Blue Angel eco-label, the term "chiller" applies to equipment:
whose refrigeration circuit is ready assembled at the factory; filling with the operating fluids (refrigerant, lubricating oil, ...) can be done at the factory or at the installation site,
Transfer liquids
whose cooling circuit was fully installed in the factory; although the machine can be filled with operating materials (refrigerant, lubricating oil, etc.) either in the factory or at the installation site,
the filling with operating materials takes place
that are electrically driven
Applied for is a: comfort chiller or process chiller with high operating temperature according to ENER Lot21 (EU Regulation 2016/2281).
that are thermally driven
Applied for: e.g. sorption refrigeration system
that are recooled via the ambient air or heat transfer fluids
Specification about the recooling:
which have a nominal cooling capacity in the range of 2 to 2000 kW.
Nominal power:
Waste heat is used
Comment:
Excludes:
Heat pumps are excluded if they fall within the scope of the Ecodesign Regulation for heat pumps up to 400 kW nominal power (EU Regulation 813/2013), even if their heat source is connected via liquids. Heat pumps with a rated power above 400 kW are also excluded.

## Requirements
Eco-label for "Chillers"
Annex 1 to the contract according to DE-UZ 231 | The applicant confirms compliance with the requirement | The applicant confirms that this requirement does not need to be met | Additional attachments | Comment field
3.1 Refrigerant
The chillers are free of halogenated refrigerants
Data sheet of the chiller with specification of the refrigerant and filling quantity is submitted
Filling quantity:
SDS is attached
3.2 Energy efficiency
3.2.1 Electrically driven chillers
Electric chillers shall provide the minimum seasonal efficiencies listed in Table 1 of DE-UZ 231 at nominal chilled water conditions of 12/7 °C, depending on the re-cooling type and capacity range. If the chillers cannot provide these temperature conditions for technological reasons, the minimum efficiencies listed in Table 2 of DE-UZ 231 apply at the standard operating conditions for chilled ceiling applications (23/18 °C)
Test report submitted with data on space cooling annual utilization rate at nominal cold water conditions 12/7 °C
Test report submitted with room cooling annual utilization factor at nominal cold water conditions 23/18 °C
Justification why cold water nominal conditions 23/18 °C
ηsc:
Indication of whether values were determined at fixed or variable outlet temperature at the evaporator:
For a series of chillers, the applicant shall meet the requirements for at least one chiller, but at the same time shall meet at least 25% of the models in the series that also apply to individual chillers
The design documents of all models of the series are submitted
3.2.2 Thermally driven chillers (absorption chillers)
Thermally driven chillers should be certified for
EER SKM+RK is:
Calculation in the next spreadsheet
3.3 Noise emissions
for electric chillers the compressor integration is vibration decoupled (internal or external)
The applicant states that the following measures have been taken to reduce noise emissions from the chiller:
Two-stage bearings for the compressor with an oscillating plate
Noise absorption hood for the compressor
Soundproofing of the housing
Vibration-isolated installation of the compressor
Vibration-isolated installation of the liquefier
Chiller fitted with vibration-isolated installation points or feet as standard
Soundproofing of the power electronics against high frequencies
Avoidance of certain (resonance) frequencies using control technology
Low-noise operating mode with reduced performance and/or efficiency
Vibration-isolated liquid connections (no rigid couplings)
Use of bulkheads
Other measures:
For air-cooled chillers, the following options must also be specified:
Sound barrier between compressor and air duct
Sound-optimized fan geometry
Fans with diffusers
Oversizing of fans for operation at low speeds
Installation instructions with details of the measures that can be taken on site to reduce noise, the boundary conditions that must be observed and how the measures may affect the performance or efficiency of the chiller must be submitted with reference to the relevant passages. Please mark the passages in color.
3.4 Requirements placed on the manufacturing process
The applicant confirms that the chiller complies with all applicable German and European specifications.
The applicant confirms that in the case of exemptions under EU Regulation 2011/65 (RoHS, here Article 4, Annex III and Annex IV, as well as subsequent adaptations, e.g. under Regulation 2019/172) regulated substances claimed by the manufacturer, RAL will be communicated and declared."
The applicant confirms that the claimed exemptions to the above regulations are also available with the product documentation on the manufacturer's homepage.
The applicant confirms that:
Spare parts (or comparable, with minor adjustments) are available for at least 10 years
good reparability (during service life) and dismantlability (at end of life) are criteria in product development
3.5 Ensuring efficient operation
3.5.1 Installation, commissioning and maintenance instructions
The applicant confirms that the chillers are supplied with detailed installation, commissioning and maintenance instructions.
The installation, commissioning as well as maintenance instructions have been uploaded, alternatively link to the instructions in the comment field.
The applicant confirms that the maintenance instructions address all points of the VDMA 24186-1:2019-09 "Performance program for the maintenance of technical systems and equipment in buildings - Part 3: Refrigeration equipment and systems for cooling and heating purposes" that are relevant for chillers, provided that they are independent of the application or the installation site.
3.5.2 Ability for the manufacturer to remotely access the chiller
The applicant confirms that the chiller is offered at least optionally with an interface for remote access to the following parameters:
For electrically driven chillers:
Inlet and outlet temperatures of all external media circuits (cold water, cooling water for water-cooled chillers)
For air-cooled chillers: Ambient air temperature
Pressure in evaporator and condenser
Compressor speed
Internal fault and status messages
For thermally driven chillers:
Inlet and outlet temperatures of all external media circuits (hot, cooling and cold water)
Internal fault and status messages
Attached is a data sheet specifying the interface for remote access
general comment

## Calculation EER (thermal)
Calculation of the EER SKM+RK plant-specific EER of the sorption refrigeration plant including drycooler
Calculation of the EERSKM+RK according to the equation below, indicating all input values and their origin. For measured values, the measurement inaccuracy must also be specified.
#DIV/0!
Specification of parameters (numbers only) |  | Measurement inaccuracy | Origin of the data
W
COP
∆pHT | Pa
∆pMT | Pa
∆pNT | Pa
VHT | m³/s
VMT | m³/s
VNT | m³/s
Pel,int: | W
Note on A8: Referenzkälteleistung bei den o.g. Bedingungen in W
Note on A9: Wärmeverhältnis (Kälte- zu Antriebsleistung) bei Nominalbedingungen
Note on A10: maschineninterner Druckverlust der Sorptionskälteanlage im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in Pa
Note on A11: maschineninterner Druckverlust der Sorptionskälteanlage im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in Pa
Note on A12: maschineninterner Druckverlust der Sorptionskälteanlage im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in Pa
Note on A13: Nominaler Volumenstrom im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in m³/s
Note on A14: Nominaler Volumenstrom im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in m³/s
Note on A15: Nominaler Volumenstrom im Antriebskreis (HT), Rückkühlkreis (MT) bzw. Kaltwasserkreis (NT) in m³/s
Note on A16: Elektrische Leistungsaufnahme der Kältemaschine bei o.g. Betriebspunkt (Regler, interne Pumpen, etc.) in W

## Table2
factory-supplied
at the installation site
internal
external